## Front Cover
Specification and Contract Sum Analysis
191B Park Drive (Nebula)
Milton Park
Oxfordshire
Milton Park
OX14
Fit-out works
21st August 2026
Tender Issue

## Contents
Contents
1. General Requirements
2. Preliminaries
3. Design Fees
4. Scope of Works - Building Fabric / Architectural
5. Scope of Works - MEP Installations
6. Scope of Works - FF&E
7. Collection and Tender Summary

## 1. Gen Requirements
Contract sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
1 | General Requirements
To be read in conjunction with all of the Employers Requirements documents
1.1 | Building 191B is located off Park Drive, Milton Park, Oxfordshire, OX14 4SA. The site is situated between Oxford and Reading near to Abingdon and Didcot and just off the A34.
1.2 | The project's objective is to fit-out the property to a Cat B standard to provide a suitable workplace for the Employer, GenScript Biotech Limited.
1.3 | The project generally comprises the design and construction of the following works:
Installation of demountable partitioning and doors to create cellular space with the warehouse and office space comprising the follow: GF: Inbound/outbound, packing area, Dry Ice/LN2 store multi-function room, storage, printer room, meeting rooms, FF: meeting rooms, open office
Installation of suspended ceilings to targeted ground floor areas.
Construction of new electrical DB cupboard
Surface sealant treatment to warehouse space
FF&E
Decoration to all areas save for the staircore.
New external personnel door to the front elevation
Compound fence to house new external AC units
2No new teapoints and associated services
New HVAC to ground floor cellular space
Modify and expand existing first floor HVAC
New lighting and controls throughout
Modify and extend existing fire alarm system
New electrical distribution and containment
IT/network installations
Gas monitoring system to LN2 store
Fire stopping works
Security/intruder alarm system
Access control
The Building
1.4 | The building is a timber Glulam framed with composite metal deck first floor. The ground floor is of a solid ground bearing concrete slab. The external facade comprise a built up insulated rainscreen cladding system finished with various different materials including vertical PVC coated steel cladding sheets, vertically mounted larch timber planks, projecting anodised bronze aluminium sheets and polyester powder coated (PPC) aluminium curtain walling with double glazed units. The building occupies the middle unit of three terraced units of matching construction. The unit to the right (191C) is occupied by Inify Laboratories. The unit to the left, is vacant. Tarmacadam surfaces and block paving are provided to the front of the building and access road. The building was constructed in 2024 and has not been occupied since completion and is therefore in 'as new' condition. Existing O&M/as-builts drawings and H&S file are available and included within this tender pack.
General Notes
1.5 | The contractor is to fully familiarise themselves with the building during pricing.
1.6 | The contract is to be procured under the JCT Design and Build 2024 contract and will be subject to a Schedule of Amendments (Special Conditions). Draft copies of have been provided within this this tender pack.
1.7 | The contractor shall price each and every clause individually on an elemental basis. All non-priced clauses will be deemed to be included in the general pricing of the works.
1.8 | All Provisional Sums (PS) and quantities in this schedule are to be expended at the sole discretion of the QS. Where PS are specified, the QS is to confirm actual costs once the works are known and detailed. The contractor is to obtain written agreement to provisional work items prior to commencing the works.
1.9 | In the event that discrepancies arise between the details set out in this schedule and those contained within the contract drawings then the schedule shall take priority.
1.1 | The Contractor is to submit an project programme as part of the tender return.
1.11 | In the event of any arithmetical errors, the overall price will be dominant.
1.12 | The building is currently vacant.
1.13 | Contractor parking is restricted to car parking spaces demised to building 191B. Additional car parking may be available should this be deemed necessary upon agreement with the EA.
1.14 | The Contractor is to fulfil the role of 'Principal Designer' Under the Building Regulations and will be responsible for signing the Building Regulations declaration and conformity on completion of the project.
1.15 | The Contractor will fulfil the role of Principal Designer under the Construction Design Management regulations following their appointment. T&T PJM UK will provide this role during the pre-contract stages only.
1.16 | The contractor will carry out a Photographic schedule of condition prior to commencement of the works to the external areas and main vehicular access route.
1.17 | The Contractor will be deemed to have inspected the existing retained structure and fabric and to have accepted the existing retained structure and fabric as suitable to accommodate the works. The contractor will be required to carry out all adaptions to the existing structure and fabric as necessary to achieve the Employers Requirements
Procedures and Working Practices
1.18 | Should the EA be dissatisfied with an employee of the Contractor or their appointed Sub Contractor, they shall give notice thereof in writing. The Contractor shall, within 48 hours, discharge such operative and substitute with another.
1.19 | The contractor as part of the works is to agree procedures and working practices with the EA in order to ensure that the client is not held liable for any incidents arising from the project works.
1.2 | The Contractor is to allow sufficient resource and facilities for a site meeting fortnightly throughout the contract period, along with ad-hoc inspections by the EA and/or other interested parties. Contract Progress meetings will be held monthly and the Contractor will be expected to issue a progress report for this meeting.
1.21 | The contractor will be permitted to use the existing welfare facilities during the course of the works but must ensure that all facilities are handed over on completion in 'as new' condition. The contractor will be responsible to make good any damage caused to the exiting building during the course of their works.
1.22 | All temporary access (internal platforms etc.) and protection required for the execution of the works shall be included and organised by the Contractor.
1.23 | The Contractor is responsible for submitting appropriate notices to the Local Authority, obtaining licenses, arranging inspections and paying all fees/charges, etc. associated with the execution of the works.
1.24 | The contractor must provide comprehensive temporary protection of the retained building fabric to ensure this is not damaged during the course of their works. Any damage will be responsibility of the contactor to remedy. This is particularly pertinent to the core area which is not being altered or redecorated. These areas must be handed over in their current 'as new' condition.
1.25 | All dismantling, demolition, stripping out and removing of items described herein is deemed to include any necessary making good, or, replacing components damaged by the removal works, whether specified elsewhere or not.
1.26 | All instructions are to be given via the EA instructions only. Should the EA change during the project, notification in writing will be provided to the contractor either by the EA or by a senior member of the CBRE Team.
1.27 | The Contractor shall have full responsibility for all aspects of site set up, management of works on site and control of the programme to ensure that quality and progress of works achieve the agreed standards
Working Hours
1.27 | Normal operating hours are 08.00 to 18.00 Monday-Friday (subject to confirmation from the Facilities Manager). Requests will need to be submitted in advance for out of hours working.
1.28 | Noisy works will need to be managed, and particularly noisy works done out of hours. Given the adjoining unit is occupied, the contractor will need to make a sensible allowance for out of hours working within the tender submission.
Health and Safety
1.29 | The Principal Designer on the Project shall be Turner & Townsend PJM UK Limited, contact Ben Haynes / Elizabeth Caton (details identified within the preliminaries)- Pre -contract only. The expectation is that this role will then be undertaken by the Main Contractor or an approved third party upon appointment of the contactor.
1.3 | The Contractor is to develop a Construction Phase Health and Safety Plan which is to be submitted to the Principal Designer for review one week before works commence on site. The Contractor is to submit a full Health and Safety File for the works within 5 working days of Practical Completion. The Contractor is to be in compliance with the CDM Regulations (2015) at all times and is to report to the Principal Designer and provide all information within requested timescales.
1.31 | The Contractor is to ensure all employees are adopting safe working methods in accordance with risk assessments and method statements. Safe systems of work must be established by the Principal Contractor and meet with the building manager's requirements. The Contractor is also to ensure that employees wear appropriate PPE at all times.
1.32 | All visitors to the site including sub-contractors employed to work on the site are to undergo a site induction, which will be the Contractor's responsibility.
1.33 | The contractor is to report to the EA, Principal Designer, and Building Manager at the earliest opportunity, any accidents or incidents that result or could have resulted in injury or harm to employees or the general public.
1.34 | The building was constructed in 2024 and therefore has no requirement for asbestos surveys.
Materials and Workmanship
1.35 | All specified materials are described within the schedule of works and are to be of a good standard and suitable for use within the works area. The materials, fittings and equipment to be used shall be selected as a quality suitable for their intended purpose and to meet the requirements and approval of the Employer. Standards and quality shall be consistent throughout.
1.36 | All workmanship will be undertaken in a high quality, good and appropriate manner.
Record Drawings, Operation and Maintenance Manuals
1.37 | A full Operation & Maintenance Manual must be provided by the Contractor within 1 week of Practical Completion.
1.38 | The Contractor will be required to produce all required coordinated drawings for presentation, statutory approvals & O&Ms.
Facilities
1.39 | Power and water can be utilised from the property, however the Contractor is to investigate how best these can be utilised and agree prior approval from the client. The contractor should liaise with Building Management in this regard. Meter readings will need to be provided prior to commencement.
Programme
1.4 | Refer to Instructions to Tenderers document for outline programme.

## 2. Prelims
Contact Sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
2 | Preliminaries
Item | Description | Quantity | Unit | Rate | Total
2.1 | Management staff cost | 26 | Days | 200 | 5200
2.2 | Site manager/foreman | 68 | Days | 300 | 20400
2.3 | Labourer | 13 | Days | 150 | 1950
2.4 | Site welfare | 13 | Weeks | 150 | 1950
2.5 | Site accommodation | 13 | Weeks | 120 | 1560
2.6 | Security
2.7 | Hoarding
2.8 | Plant hire
2.9 | Scaffold/access costs | 1 | Item |  | 6500
2.10 | Skips & Waste management
2.11 | Temporary services | 1 | Item |  | 1200
2.12 | Temporary protection | 1 | Item |  | 1600
2.13 | Site signage | 1 | Item |  | 1300
2.14 | Health & safety & CDM | 1 | Item |  | 5323
2.15 | Performance bond |  |  |  | Included
2.16 | Joint fire code | 1 | Item |  | 25000
2.17 | Access equipment | 1 | Item |  | 1200
2.18 | Out of hours working allowance
2.19 | Other
| PRELIMINARIES TOTAL |  |  |  | 73183

## 3. Design Fees
Contact Sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
3 | Design Fees
Item | Description | Quantity | Unit | Rate | Total
3.1 | Design development fees, including: Drawings updates to develop existing drawings up to Stage 5 - 6. | 1 | Item | 2500 | 2500
3.2 | License to Alter support; Planning consultant as application; As-built drawings to handover | 1 | Item | 1200 | 1200
3.3 | Architectural drawings | 1 | Item | 2100 | 2100
3.4 | MEP drawings | 1 | Item | 2400 | 2400
3.5 | Fire Engineer Assessment Report and fully detailed fire strategy | 1 | Item | 12500 | 12500
3.6 | Principal Designer fees (CDM) | 1 | Item | 4500 | 4500
3.7 | Principal Designer fees (Building Regulations) | 1 | Item | 1200 | 1200
3.8 | Building Control | 1 | Item | 3100 | 3100
3.9 | EPC assessment | 1 | Item | 2100 | 2100
3.1 | Performance bond | 1 | Item | 9000 | 9000
3.11 | DSEAR and COSHH Assessment, LN2 Risk Assessment | 1 | Item | 4100 | 4100
3.12 | Acoustician Assessment | 1 | Item | 2875 | 2875
3.13 | Structural Engineer fees (if required) | 1 | Item | 1747.05 | 1747.5
3.14 | Others(add here and below if any)
| DESIGN FEES TOTAL |  |  |  | 49322.5

## 4. SoW - Fabric
Cost sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
4 | Scope of Works - Builders Works
NB: All instructions are to be given through the Employers Agent only.
Item | Building Works | Quantity | Unit | Rate | Total | Bidding Brands (One or more)
4.1 | STRIP OUT WORKS
4.1.1 | Strip out and store carpet floor finishes on the first floor, remaining carpet floor to be stacked on site for reuse. | 1 | item | 1 | 2500
4.1.2 | Other miscellaneous strip out works as required. |  |  |  | 0
4.2 | EXTERNAL WORKS
4.2.1 | Remove glazed curtain wall panel from existing window opening (adjacent shutter door), and reveal cladding, trim out opening providing suitable structural support for new opening size, cut out timber cladding at low level to form new opening. Insert new powder coated aluminium door with glazed panel to match existing. Include for new secondary steel work and a new glazed curtain wall panel above the door to fill the reduced opening size. Instate brise solei cladding Forming the opening for the new external door; incl. cutting the external wall and dispose debris off site, making good of the external cladding and new door reveals | 1 | PC SUM | 25000 | 25000
4.2.2 | Supply and install new external glass door; to match existing; single leaf door; incl. removal of the existing frame, storage of removed items at a location TBC by landlord; supply and install new frame with glass screens as single leaf door | 1 | Item | 6500 | 6500
4.2.3 | Supply and install Hit & Miss type timber fence to plant compound | 1 | Item | 2300 | 2300
4.2.4 | Concrete base for additional external condensing units. | 1 | item | 1500 | 1500
4.2.5 | Others(add here and below if any) |  |  |  | 0
4.3 | INTERNAL PARTITIONS
4.3.1 | The contractor is refer to drawing 5208 A102 for indicative partition layout and types. |  |  |  | 0
4.3.2 | Allowance for making good of the internal lining reveals for new external door to the front elevation. |  |  |  | 2599
First Floor (3No meeting rooms)
4.3.4 | BG GypWall Single Frame A206035 (EN), 49dB; 100mm thickness (50mm frame); 2x12.5mm standard plasterboard each side; 25mm insulation; slab to steel frame (up to 3200mm high); head bracing detail; tape and joint finish; fixing accessories between rooms (shown black on drawing 5208 A102) | 21 | lm | 288.65 | 6061.65
4.3.5 | Aluminium frame; 2100mm high (approx.) ; toughened single glazed; NFR; 40dB; incl. fixing accessories Silicon jointed glazed partitions to front walls with stud/plasterboard bulkhead above to meet ceiling lid. | 4 | lm | 662 | 2649.6
Ground Floor
4.3.6 | Drywall partition to GF Printer Rm: BG GypWall Single Frame A206015 (A) (EN), FEI30, 45dB+; 122mm thickness (72mm frame); 2x12.5mm standard plasterboard each side; 25mm insulation; slab to steel frame (up to 3800mm high); deflection head detail; tape and joint finish; fixing accessories | 17 | lm | 506 | 8602
4.3.7 | Drywall partition to GF Meeting Rm 2 (shown black on drawing 5208 A102): BG GypWall Single Frame A206015 (A) (EN), 45dB+; 122mm thickness (72mm frame); 2x12.5mm standard plasterboard each side; 25mm insulation; slab to steel frame (up to 3800mm high); deflection head detail; tape and joint finish; fixing accessories. Incorporate Aluminium frame; 2100mm high; toughened single glazed; NFR; 40dB; incl. fixing accessories Silicon jointed glazed partition. | 11.5 | lm | 600.3 | 6903.45
4.3.8 | Drywall partition to GF warehouse side (shown green on drawing 5208 A102): BG GypWall Single Frame A206015 (A) (EN), 45dB+; 122mm thickness (72mm frame); 2x12.5mm standard plasterboard each side; 25mm insulation; slab to steel frame (up to 3600mm high); deflection head detail; tape and joint finish; fixing accessories. | 47 | lm | 585.35 | 27511.45
4.3.9 | Drywall partition between Warehouse area / Office (shown blue on drawing 5208 A102): BG GypWall Single Frame A206015 (A) (EN), FEI30, 45dB+; 122mm thickness (72mm frame); 2x12.5mm standard plasterboard each side; 25mm insulation; slab to steel frame (up to 3600mm high); deflection head detail; tape and joint finish; fixing accessories. | 50 | lm | 477.25 | 23862.5
4.3.10 | Include extra over cost to supply and install Isover 50mm acoustic partition roll to all newly created partitions. | 490 | m2 | 2.3 | 1127
4.3.11 | Supply and install encasement to steel columns; type TBC; up to 3400mm high | 1 | PC Sum | 5750 | 5750
4.3.12 | Supply and install fire encasement to steel columns; FEI30; | 1 | PC Sum | 8050 | 8050
4.3.13 | Pattressing to partitions, incl. fixing accessories | 12 | lm | 54.05 | 648.6
4.3.14 | Galvanised I studs or similar to provide additional support to partitions (indicated by red squares on drawing 5208 A102) | 31 | nr | 345 | 10695
4.3.15 | Supply and install acoustic barriers under raised floors to first floor partitions. | 21 | lm | 23 | 483
4.4 | DOORS & WINDOWS
Doors
4.4.1 | 5No double steel doors with single vision panel (with door frame, hinge, lock, etc) to warehouse partitions. | 5 | nr | 4025 | 20125
4.4.2 | 7No single steel door with single vision panel (with door frame, hinge, lock, etc) | 7 | nr | 3007.25 | 21050.75
4.4.3 | Indicate cost saving for solid core fully sealed laminate faced doors with oak lippings throughout the warehouse with 2No vision panels throughout £_____________________________
4.4.4 | 6No. single solid core timber veneered door with 2No vision panel (with door frame, hinge, lock, etc) | 6 | nr | 1828 | 10968
4.4.5 | High speed roller shutter door to Dry Ice / LN2 Store; 1500x2100mm; type Dynaco D-313 or equivalent; automated opening; safety closing mechanism; push button both sides, including all associated electrical works. |  |  |  | 0
4.4.6 | Mechanical equipment cupboard. | 1 | PC Sum | 2300 | 2300
4.4.7 | Electrical equipment/switchgear/DB's cupboard. | 1 | PC Sum | 5250 | 5250
Windows/Screens
4.4.8 | Glass screen to Inbound/Outbound Shipping Area and Open Office 2: Aluminium frame; 1200x1200mm; Single glazed; NFR; 40dB; incl. fixing accessories | 1 | item | 920 | 920
4.4.9 | Painting new door frames |  |  |  | 0
4.4.10 | Others(add here and below if any) |  |  |  | 0
4.5 | JOINERY
4.5.1 | GF Kitchenette: Howdens Clerkenwell Super Matt White; 3700mm units; laminate worktop; integrated bins; Lamona sink/tap/fridge as indicated on drawing 5208 A200 | 1 | PC Sum | 12592.5 | 12592.5
4.5.2 | FF Kitchenette: Howdens Clerkenwell Super Matt White; 2500mm units; laminate worktop; integrated bins; NO sink/tap; built-in fridge as indicated on drawing 5208 A200 | 1 | PC Sum | 6417 | 6417
4.5.3 | Include extra over cost to 4.5.2 for sink/tap and associated domestic services (drainage, H&C supply, extraction) |  |  |  | 0
4.6 | CEILING FINISHES
4.6.1 | The contractor is to refer to drawing 5208 A103 for indicative ceiling types/RCP. |  |  |  | 0
First Floor
4.6.2 | Ceiling lid to FF 3No meeting rooms: Partition framed; "I" joists, NFR; 1x15mm standard plasterboard; tape and joint; incl. trims and accessories (no suspended grid). | 40 | m2 | 230 | 9200
4.6.3 | Extra over cost to 4.6.2 to suspend 600 x 600m ceiling grid with mineral fibre tile below the plastered lid. | 40 | m2 | 60.95 | 2438
Ground Floor
4.6.4 | Ceiling lid with 600x600m suspended grid and mineral fibre tiles to all newly formed areas except Meeting Room 1 and Teapoint/Pantry which have existing plastered ceiling beneath the mezzanine. Include all necessary trims, hangers, fixings, accessories as required. | 208 | m2 | 60.95 | 12677.6
4.6.5 | Plastered ceiling lid only to the inbound/outbound shipping area. | 17 | m2 | 103.5 | 1759.5
4.6.6 | Include optional cost for encapsulated "black bagged" acoustic insulation above newly formed cellular room meeting rooms. | 30 | m2 | 34.5 | 1035
4.6.7 | Trim out penetration detail around shutter door to allow door to pass through Shipping lid. | 4.5 | lm | 89.7 | 403.65
4.6.8 | Support for M&E and grid under Mezzanine, incl. reinstatement of FEI60 ceiling. | 1 | nr | 1150 | 1150
4.6.9 | Supply and install ceiling margin bulkhead details to GF Open Office 2; incl. framework, trims | 6 | lm | 138 | 828
4.6.10 | Allowance for pattressing to ceilings, incl. fixing accessories. | 1 | PC Sum | 345 | 345
4.6.11 | Others(add here and below if any). |  |  |  | 0
4.7 | WALL FINISHES/DECORATION
4.7.1 | Tile splashbacks to GF and FF Kitchenettes; tile cost up to £50/m2; incl. trims and accessories. | 2 | Item | 2100 | 4200
4.7.2 | Decorate existing wall areas as shown on drawing 5208 A106. | 200 | LM | 8.2 | 1640
4.7.3 | Extra over 4.7.2 to redecorate all existing areas not included in the item 4.7.2.. |  |  |  | 0
4.7.4 | Decorate all newly formed partitions. | 412.5 | LM | 10 | 4125
4.7.5 | Decorate skirting board to match existing |  |  |  | 0
4.7.6 | Decorate painted plastered ceilings. | 1 | Item | 5500 | 5500
4.7.7 | Decorate door frames. | 22 | No | 160 | 3520
4.7.8 | Redecorate existing skirting boards. | 1 | Item | 4300 | 4300
4.7.9 | Allowance for mastic finishes all typical areas. | 1 | Item | 1670 | 1670
4.7.10 | Others(add here and below if any)
4.7.11 | Provide statutory signage as required throughout the property. | 1 | Item (Prov Sum) |  | 6500
4.8 | RAISED FLOORS
4.8.1 | Modify existing first floor raised floor panels to accommodate new MEP services |  |  |  | 1500
4.8.2 | De-rock existing panels as required. |  |  |  | 1200
4.8.3 | New floor boxes an grommets as required. |  |  |  | 1320
4.9 | FLOORING FINISHES
4.9.1 | Allowance to reinstate FF carpet tiles. | 102 m2 | 6.22 |  | 634.44
4.9.2 | Latex screed to GF areas to newly formed areas, | 102 m2 | 11.99 |  | 1222.98
4.9.3 | Carpet to GF: Desso Essence or equivalent; over latex; incl. adhesive and transition trims | 108 m2 | 20.82 |  | 2248.56
4.9.4 | Vinyl to FF Teapoint: Polyflor Affinity 255 LVT or equivalent; over raised floor; incl. 6mm plywood | 5 m2 | 78.87 |  | 394.35
4.9.5 | Vinyl to GF Teapoint: Polyflor Affinity 255 LVT or equivalent; over latex | 15 m2 | 64.01 |  | 640.1
4.9.6 | Hardened Flooring with Clear Sealant - Suitable for heavy loading - Sika Dustproofer (Concrete Surface Hardener) or similar | 1 | item |  | 4100
4.9.7 | Skirtings |  |  |  | 0
4.9.8 | Others(add here and below if any) |  |  |  | 0
4.1 | FIXINGS, FITTINGS AND EQUIPMENT
4.10.1 | Provide statutory signage as required throughout the property. |  |  |  | 0
4.10.2 | Provisional sum for tenant specific signage | 1 | item | 0 | 0
4.10.3 | Refer to FF&E schedule (tab 6) |  |  |  | Note
4.11 | CLEANING
4.11.1 | Carry out sparkle clean on completion of works throughout the whole of the property. | 1 | Item | 1800 | 1800
4.12 | BUILDERS WORKS IN CONNECTION TO SERVICES
4.12.1 | Steel frame and purlins for ceilings/M&E: Open Office and Warehouse Storage areas | 1 | Item (Prov Sum) |  | 35000
4.12.2 | Penetrations through cladding for M&E services | 1 | Item | 2890 | 2890
4.12.3 | Replace glass screens with insulated panels for M&E outlets |  |  |  | 0
4.12.4 | General BWIC |  |  |  | 2300
4.12.5 | Firestopping |  |  |  | 7500
4.12.6 | Others(add here and below if any) |  |  |  | 0
| Total |  |  |  | 346408.68
BUILDERS WORKS TOTAL

## 5. SoW - MEP
Contact Sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
5 | MEP Installations
NB: All instructions are to be given through the Employers Agent only.
Item | Building Works | Quantity | Unit | Rate | Total | Bidding Brands (One or more)
5.1 | Electrical installations
|  | 1 | 11150 |  | 11150
5.1.1 | LV Distribution Alterations & Additions
|  | 1 | 21275 |  | 21275
5.1.2 | Primary Containment
|  | 1 | 33350 |  | 33350
5.1.3 | General Power
|  | 1 | 10350 |  | 10350
5.1.4 | Mechanical Power
|  | 1 | 78200 |  | 78200
5.1.5 | Lighting & Controls
|  | 1 | 20010 |  | 20010
5.1.6 | Fire Alarm System
0
5.1.7 | Access Control & CCTV System including the following components:
0
5.1.7.1 | Desktop PC (Intel Core i5, 13th generation or later / 16GB DDR4 RAM / 512GB SSD / RTX 5060 Ti 16GB, 24-inch monitor, including operating system) & equipped with access control management software and CCTV management software
0
5.1.7.2 | 24 Ports POE switch for AP(Aruba 6200F 48G Class 4 PoE 4SFP+ 740W Switch)
0
5.1.7.3 | UTP Cat 6a 24 ports patch panel
0
5.1.7.4 | RJ45 patch cable CAT6(2m)
|  | 1 | 8625 |  | 8625
5.1.7.5 | UTP Cat 6
0
5.1.7.6 | Ø20 Conduit
0
5.1.7.7 | Bullet CAM: 4MP, 1/3" CMOS, 0.005 Lux, IR, PoE, IP66,f=4mm
0
5.1.7.8 | Dome CAM: 4MP, 1/3" CMOS, 0.005 Lux, IR, PoE, IP66,f=4mm
0
5.1.7.9 | NVR: 16-8MP channel input, 8 SATA HDD bays, .Decoding: 8×1080P,Bandwidth: 160/80 Mbps (in/out),HDMI 4K output
|  | 1 | 6808 |  | 6808
5.1.7.10 | 8TB HDD
|  | 10 | 1897.5 |  | 18975
5.1.7.11 | ACCESS CONTROLLER including CARD READER, MAGNETICALLY OPERATED PROTECTIVE SWITCH, ELECTRIC LOCK AND DOOR CONTACT, REQUEST EXIT DEVICE, GLASS BROKEN BUTTON, power adapter & all related wirings among these components.
|  | 5 | 379.5 |  | 1897
5.1.7.12 | Cards (Preventing NFC-cloned )
0
5.1.7.13 | Data outlet connecting to Desktop PC
0
5.1.7.14 | AC power electric wirings (RVV) 3*1.0 (from GF Server Rack of IT system to all access controllers)
0
5.1.7.15 | Information of CCTV System to be connected to local authority side including including documentation application work & permits etc. to meet codes/compliance
0
5.1.7.16 | Others(add here and below if any)
|  | 1 |  |  | 13800
5.1.9 | UPS - Warehouse Uninterrupted Power (10kVA SPN system, 60min)
|  | 1 |  |  | 2070
5.1.10 | Testing & Commissioning | 1
|  | 1 | 10465 |  | 10465
5.1.11 | Others(add here and below if any)
5.2 | Mechanical installations
0
5.2.1 | Dehumidifer (> 10kg/h (240L/D) dehumidification capacity,ductwork,air terminal devices, thermal insulation, condensate water drainage piping) | 1 |  | 3450 | 3450
5.2.2 | LN2/Dry Ice Extraction: Fan/control (10-20 ACH); extract ductwork low level to façade; make-up return air grilles from warehouse |  | incl 5.4.2. |  | 0
5.2.3 | Roller Shutter Air Curtain: Electric overdoor heater and controller to the roller | 1 |  | 2070 | 2070
5.3 | DOMESTIC WATER SERVICES
5.3.1 | Above Ground Drainage: Waste pipework (pumped) to existing stack in GF WC; point of use water heaters to GF teapoint/lobby basin | 1 |  | 5060 | 5060
5.3.2 | Oxygen Depletion Alarms: CO2 detection in Packing/LN2 area; audio visual beacons/detectors | 1 |  | 977.5 | 977.5
5.3.3 | Oxygen Depletion Alarms: O2 detection in Packing/LN2 area; audio visual beacons/detectors | 1 |  | 977.5 | 977.5
5.3.4 | Testing and Commissioning: Ventilation flow rates; DHW temps; chlorination; mechanical system testing; O as-builts | 1 |  | 5175 | 5175
5.4 | HVAC Option 1
5.4.1 | Validation of existing: Recording duties of 2no. MVHR; VRF operational checks; visual inspections | 1 |  | 2530 | 2530
5.4.2 | Ground Floor Office Ventilation: New MVHR unit; supply and extract ductwork; attenuation; air terminal devices; thermal insulation | 1 |  | 75900 | 75900
5.4.3 | First Floor Office Ventilation: Modifications to existing MVHR (Note: System is 50l/s short of future max occupancy) |  | incl 5.4.2 |  | 0
5.4.4 | Ground Floor VRF Air Conditioning: 1no external condenser and 7no ducted fan coils; local controls; refrigerant and condensate pipework | 1 |  | 66700 | 66700
5.4.5 | First Floor VRF Air Conditioning: De-gassing; removal of 1 fan coil; 3no new ducted units and associated controllers |  | incl 5.4.4 |  | 0
5.4.6 | Packing Area Cooling: Dedicated DX split unit (1 indoor and 1 external unit) | 1 |  | 6014.5 | 6014.5
5.4.7 | Central VRF Control Updates: Inclusion of new MVHR/VRF to existing central controller | 1 |  | 3277.5 | 3277.5
5.5 | HVAC Option 2
0
5.5.1 | Direct Expansion Air Conditioning Units (with cooling & heating functions, including all refrigerant media & copper tubes & insulation, wiring, and controllers , procurement, commissioning, handover)
0
5.5.2 | Others(add here and below if any)
5.6 | M&E OPTIONS
0
5.6.1 | Provisional Sum - Power provision for future PV System
0
5.6.2 | Extra Over for LEV Ventilation (2 arms) to Packing Area: 2no LEV arms; inline extract fan; ductwork to façade; powered closed motorised dampers; controls; Provisional Sum for power
0
5.6.3 | Others(add here and below if any)
5.7 | IT SYSTEM
0
5.7.1 | 24 Ports POE switch for AP(Aruba 6200F 48G Class 4 PoE 4SFP+ 740W Switch) |  | Included
|  |  | Included |  | 0
5.7.2 | 48 Ports switch for data/IP tele outlet(Aruba JL676A 6100 48G 4SFP+ Switch) |  | Included
|  |  | Included |  | 0
5.7.3 | UTP Cat 6a 24 ports patch panel |  | Included
|  |  | Included |  | 0
5.7.4 | RJ45 patch cable CAT6(2m) |  | Included
|  |  | Included |  | 0
5.7.5 | UTP Cat 6 |  | Included
|  |  | Included |  | 0
5.7.6 | Ø20 Conduit for AP |  | Included
|  |  | Included |  | 0
5.7.7 | Ø25 Conduit for data/IP tele outlet |  | Included
|  |  | Included |  | 0
5.7.8 | Ø20 Conduit for data/IP tele outlet |  | Included
|  |  | Included |  | 0
5.7.9 | Cable tray 150*100mm for IT wiring |  | Included
|  |  | Included |  | 0
5.7.10 | Normal Access Point (AP) (Aruba AP615 ) |  | Included
|  |  | Included |  | 0
5.7.11 | Wireless Mobility Controller: ArubaOS (MODEL: Aruba9012-US), Version 8.12.0.6 SSR (alternatively, a Cloud AP solution can be used) |  | Included
|  |  | Included |  | 0
5.7.12 | Data/IP tele outlet |  | Included
|  |  | Included |  | 0
5.7.13 | Optic fibre of Upstream Internet from outside |  | Included
|  |  | Included |  | 0
5.7.14 | Ø32 Imbedded HDMI Conduit & Wiring |  | Included
|  |  | Included |  | 0
5.7.15 | Others(add here and below if any) |  | Included |  | 0
|  |  |  | To summary | 409107
MEP TOTAL

## 6. SoW - FFE
Contact Sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
6 | Furniture, Fixtures and Equipment (FF&E)
NB: All instructions are to be given through the Employers Agent only.
Item | Building Works
6.1 | FF&E
ID | ITEM | QTY | Unit | Rate | Total | Supply | Transport | Install | Technical Requirements
GF-O | GROUND FLOOR - OFFICES | [7 empty] | Referred Photo | Description of Technical Requirements
18.1 | RECEPTION
18.2 | PRINT ROOM
18.3 | TEAPOINT & PANTRY
18.3.1 | Kitchenette base + wall cabinets | 1 |  |  |  | Y | Y | Y | Specs and measures should be defined by contractor based on area measurements. | Specs and measures should be defined by contractor based on area measurements.
18.3.2 | Sink + tap | 1 |  |  |  | Y | Y | Y | Specs and measures should be defined by contractor based on area measurements. | Specs and measures should be defined by contractor based on area measurements.
18.3.3 | Dishwasher | 1 | Item | 950 | 950 | Y | Y | Y | SMS26AW08G Free-standing dishwasher ¦ BOSCH GB | Sample product. Needs to fit into base cabinet.
18.3.4 | Pure Water Dispenser | 1 | Item | 2500 | 2500 | Y | Y | Y | AQA drink PRO 20 - Water Dispensers - BWT | Sample product. Countertop model preffered.
18.4 | OPEN OFFICE 2 |  | Item
18.4.1 | Table | 8 | Item | 250 | 2000 | Y | Y | Y | Dams Rectangular Maestro 25 Desk with Twin Cantilever Legs - Office Furniture Direct | Rectangular office desk with cable management ports and scratch-resistant surface for daily office use. Sample product.
18.4.2 | Chairs | 8 | Item | 120 | 960 | Y | Y | Y | Base Mesh Office Chair from our Mesh Office Chairs range. | Ergonomic mesh office chair with adjustable headrest and lumbar support for daily office use. Sample product.
18.4.3 | Filing Cabinet | 1 | Item | 750 | 750 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%217945837_alt?hei=466&wid=466&fmt=webp | Metal filing cabinet with miüed open and enclosed storage compartments for office document organisation. Sample product.
18.5 | MANAGER OFFICE 3 |  | Item
18.5.1 | Filing Cabinet | 1 | Item | 550 | 550 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%213810180_alt?hei=466&wid=466&fmt=webp | Lockable filing cabinet with internal shelving for organised office document and storage management.
18.5.2 | Manifestation/Branding to glass partition | 1 | Item | 150 | 450 | Y | Y | Y | 3LM
18.6 | MEETING ROOM 2 |  | Item
18.6.1 | Table | 1 | Item | 2500 | 2500 | Y | Y | Y | https://kantoormeubelennederland.nl/wp-content/uploads/2025/08/Real-ellips-vergadertafel.png | 12-person meeting table with integrated cable management, suitable for collaborative meetings and conference room use.
18.6.2 | Chair | 12 | Item | 450 | 5400 | Y | Y | Y | https://assets.officereality.co.uk/uploads/BCF-8003AV-BGF-AURA-BACK-SIDE.jpg | Mesh visitor chair with fiüed armrests and sled base, suitable for meeting rooms and guest seating.
18.6.3 | Stackable chairs | 8 | Item | 100 | 800 | Y | Y | Y | https://www.officecity.nl/media/catalog/product/cache/c47d9a6315d36d4d794db4dda724e322/v/e/vergaderstoel_marseille_2_2_2.jpg | Plastic Dining Room Chair with Metal Legs
18.6.4 | Under TV cabinet | 1 | Item | 120 | 120 | Y | Y | Y | https://m.media-amazon.com/images/I/61mpDarvryL._AC_SL1500_.jpg | Mobile/Standing TV stand
18.7 | MULTI-FUNCTION ROOM |  | Item
18.7.1 | Mini-fridge | 1 | Item | 820 | 820 | Y | Y | Y | https://m.media-amazon.com/images/I/51wcnMT5XIL._AC_SL1500_.jpg | Compact 48L under-counter office refrigerator suitable for pantry and break room use.
GF-W | GROUND FLOOR - WAREHOUSE |  | Item
18.8 | LOBBY |  | Item
18.8.1 | Metal sink | 1 | Item | 120 | 120 | Y | Y | Y | https://lioninox.com/cdn/shop/files/P061470.png?v=1736333789&width=550 | 1. 304 stainless steel water sink (short side of water sink shall be no less than 500mm) & Dual use hot and cold water tap with hose & all necessary fittings; 2. Thickness of 304 stainless steel water sink shall be noless than 2 mm; 3. Cabinet under 304 stainless steel can use material like steel panel with rpoper cotaing (wood will not be accepted,
18.8.2 | Eye wash | 1 | Item | 80 | 80 | Y | Y | Y | https://webassets.lyreco.com/products/350/539/2350539.jpg?checksum=2797335809&width=640
18.8.3 | Coat hooks | 1 | Item | 180 | 180 | Y | Y | Y | https://www.manutan.nl/fstrz/r/s/www.manutan.nl/img/S/GRP/IC/AIG92571278.jpg?frz-v=31
18.9 | WAREHOUSE STORAGE - FOR ADMIN & SALES |  | Item
18.10 | WAREHOUSE STORAGE - FOR MARKETING |  | Item
18.10.1 | Heavy duty packing desk with under desk storage | 1 | Item | 1500 | 1500 | Y | Y | Y | https://www.packingtables.co.uk/wp-content/uploads/2021/10/packing-bench-1.jpg | Heavy duty packing desk with under desk storage. Suitable for weights of 100kg +
18.10.2 | Ergonomic adjustable stool | 1 | Item | 160 | 160 | Y | Y | Y | https://encrypted-tbn0.gstatic.com/shopping?q=tbn:ANd9GcR0x8vSX9FwxhUzGLeRJlFgNDdh0hVzv1A5S81vM_O1G5RpTuGnM-KRyLqLt-RBHsH4J6cz4F4sPDzBc-EN5gsg1Nvc6YgUmGkvaBNOUHp15mGx3Rkf2yjCFEFfbocYsVuAcRcMFJBd&usqp=CAc | ergonomic adjustable height stool with back support
18.10.3 | Multiple heavy duty, wall bracket support, metal standing shelves (Load rating: ≥250 kg/shelf) | 10 | Item | 550 | 5500 | Y | Y | Y | https://monstershop.co.uk/cdn/shop/files/7002_001_2nd_042c6791-a077-40f8-9adf-1867cc5540b9.jpg?v=1778108941&width=1125 | Must be load rated for at least >250kg/shelf. Ideally in total (inlcuding the box storage shelving below) approx. 10 sets of 130cm (depth) x 100cm (length) shelving.
18.10.4 | Cart trolley | 1 | Item | 240 | 240 | Y | Y | Y | www.bigdug.co.uk/bigdug-essentials-manual-scissor-lift-tables/v/BDSP150S_1/?ppc_keyword=&gad_source=1&gad_campaignid=23173480506&gclid=EAIaIQobChMIoe6Th52dkQMVy1JBAh1ZGDm8EAQYAyABEgJI1_D_BwE
18.10.5 | Literature display | 2 | Item | 410 | 820 | Y | Y | Y | www.viking-direct.co.uk/en/fas aper-36-compartment-literature-organiser-black-p-801n | Frame must NOT be plastic as it is not durable enough, needs to be either strong wood or metal. Needs to have capacity to hold at least 50 different flyers, or multiple need to be purchased
18.10.6 | Multiple heavy duty clear plastic storage boxes with lids, stackable | 4 | Item | 150 | 600 | Y | Y | Y | www.furniture-work.co.uk/media/catalog/product/cache/a36e9380f610aff10c51a9519ebca2ed/r/a/rapid_zoom_rubay7-1.jpg
18.10.7 | General waste bin | 1 | Item | 70 | 70 | Y | Y | Y | https://uk.glasdon.com/images/products/400/eco-nexus-60-duo-recycling-bin-50-50.jpg
18.10.8 | Mixed recycling bin | 1 | Item | 180 | 180 | Y | Y | Y | https://m.media-amazon.com/images/I/51xFbKYNcNL._SL1000_.jpg
18.10.9 | Anti-fatigue floor mats | 1 | Item | 210 | 210 | Y | Y | Y | https://media.kitepackaging.co.uk/images/product/large/orthomat_premium_black_and_yellow_1000_1600_HRl.jpg | Slip (DIN 51130) and fire (BS EN 13501-1) tested anti-fatigue floor mats for use at packing desk. Generally made from PVC foam or rubber. Bevelled edges to minimise trip hazard.
18.10.10 | Digital weighing package scales | 1 | Item | 350 | 350 | Y | Y | Y | https://m.media-amazon.com/images/I/71vrB5dSekL._SL1500_.jpg | Suitable for weights 1-70+kg. Whatever logistics uses would also be fine. Metal frame for long term durability.
18.10.11 | Parcel label sticker printer | 1 | Item | 230 | 230 | Y | Y | Y | https://amlabels.co.uk/media/catalog/product/cache/47e5658226c9ff6d84cf313277f30c82/c/a/capture_718_1_1.png | Zebra ZD421 Series Desktop Thermal Label Printer
18.10.12 | Step stool | 1 | Item | 165 | 165 | Y | Y | Y | https://m.media-amazon.com/images/I/61jQZOpXT6L._AC_SL1500_.jpg | metal 2 step kick step stool with anti slip, work load capacity of 150kg
18.10.13 | Box cutters | 2 | Item | 15 | 30 | Y | Y | Y | www.primetools.co.uk/wp-content/uploads/2025/07/DWHT10999-0_1.avif | safe retractable heavy duty utlility knife
18.10.14 | Heavy duty scissors | 2 | Item | 20 | 40 | Y | Y | Y | www.primetools.co.uk/wp-content/uploads/2025/01/MFS-8-Main-Image-White-BACKGROUND-scaled-686x596.jpg | heavy duty scissors suitable for use on plastic, card, etc. MUST have a bolted joint for long term durability.
18.10.15 | Packing tape in handheld roller | 2 | Item | 25 | 50 | Y | Y | Y | https://m.media-amazon.com/images/I/61jV++WhMIL._SL1080_.jpg | Whatever logistics currently uses for cross-compatibaility and ease for IT
18.10.16 | Black duck tape | 2 | Item | 10 | 20 | Y | Y | Y | https://m.media-amazon.com/images/I/8131hffd+UL._SL1500_.jpg | black duck tape
18.10.17 | Measuring tape | 2 | Item | 19 | 38 | Y | Y | Y | https://m.media-amazon.com/images/I/71wHpOfWGDL._SL1500_.jpg | a retractable measuring tape
18.10.18 | Clock | 1 | Item | 40 | 40 | Y | Y | Y | RS PRO White Radio Controlled Analogue Clock, 300 mm Diameter Wall ¦ RS | a battery operated, radio controlled (or atomic), silent (non-ticking) wall mounted clock.
18.11 | OPEN WAREHOUSE |  | Item
18.11.1 | Wall mounted Data Cabinet | 1 | Item | 250 | 250 | Y | Y | Y | https://www.cablemonkey.co.uk/73931-thickbox_default/12u-500mm-deep-2-part-wall-mounted-data-cabinet.jpg
18.11.2 | Racking | 14 | Item | 357.14 | 4999.96 | Y | Y | Y | https://images.kkeu.de/is/image/BEG/Shelving/BiG400_Shelving/BiG400_Heavy-Duty_Shelving_Mega_Deals_pdplarge-mrd--bd-B4MD1DESCb_with_Matt_black_Web.jpg?wid=1024&hei=1024 https://images.kkeu.de/is/image/BEG/Racking/Wide_Span_Racking/BiGDUG_Longspan_Shelving_Starter_Extensions_Kits_pdplarge-mrd--bd-Longspan_Galv_Extension_Bay_web.jpg?wid=1024&hei=1024 | 2 different racks: 1. BiG400 Heavy-Duty Shelving Kit 1830*610 mm, 5 Levels, Blue & Orange; total 12 standing units 2. Longspan Shelving Eütension Unit, 3000h ü 1250w ü 600d mm 300kg UDL; 2 units( 1 starter, 1 extender unit) Pls refer to below link: ht s://www.bigdug.co.uk/big400-heavy-duty-shelving-mega-deals/v/B4MD5S16_1/ ht s://www.bigdug.co.uk/bigdug-longspan-shelving-starter-eütensions-kits/v/BLS3012603EGP_1/
18.12 | DRY ICE / LN2 STORE |  | Item
18.13 | PACKING AREA |  | Item
18.13.1 | Packing bench | 2 | Item | 600 | 1200 | Y | Y | Y | BiG400 2x 4 Level Workstation Mega Deal ¦ BiGDUG | BiG400 2ü Workstation Mega Deal ¦ Melamine Worktop ¦ 1677h ü 1830w ü 610d mm ¦ Full Depth Lower Shelf ¦ 2 Top Shelves ¦ 400kg UDL ¦ Blue & Orange 2 to be purchased, 2 to be transported from Unit 9 Pls refer to below link: ht s://www.bigdug.co.uk/big400-2ü-4-level-workstation-mega-deal/v/B4WS1806MDBOM_1/
18.13.2 | Table | 1 | Item | 190 | 190 | Y | Y | Y | Plastic Folding Table ¦ Rectangular Tables¦ BiGDUG | Atlantic Rectangular Plastic Folding Tables 740h ü 1830w ü 760d mm ¦ White Pls refer to below link: ht s://www.bigdug.co.uk/office-education/education-breakout-canteen/classroom-furniture/atlantic-rectangular-plastic-folding-tables/p/EBTC27032DESC/?term=folding%20table&suggest=Atlantic%20Rectangular%20Plastic%20Folding%20Tables&articleNumber=EBCD285294_1
18.14 | CPBU |  | Item
18.15 | FREEZER AREA |  | Item
FF | FIRST FLOOR - OFFICES |  | Item
18.16 | FF CORE AREA |  | Item
18.16.1 | Phone Booths | 2 | Item | 6200 | 6200 | Y | Y | Y | Soho Office Phone Booth ¦ MEAVO Soundproof Pods & Acoustic Furniture | Please refer to the specifications for the “Soho” model via the link provided.
18.17 | TEAPOINT |  | Item
18.17.1 | Kitchenette base cabinets | 1 | Item |  |  | Y | Y | Y | Specs and measures should be defined by contractor based on area measurements. | Modular kitchenette base cabinet with integrated storage.
18.17.2 | Microwave | 1 | Item | 450 | 450 | Y | Y | Y | https://m.media-amazon.com/images/I/61XmJ0eNYJL._AC_SL1500_.jpg | 1000W, 29L interior capacity.
18.17.3 | Water dispenser | 1 | Item | 320 | 320 | Y | Y | Y | https://m.media-amazon.com/images/I/61ntNyhO9XL._AC_CR0%2C0%2C0%2C0_SX480_SY360_.jpg | Hot and chilled water dispenser for office environments.
18.18 | MANAGER OFFICE 1 |  | Item
18.18.1 | Filing Cabinet | 1 | Item | 550 | 550 | Y | Y | Y | 550https://static.viking-direct.co.uk/is/image/odeu13/%213810180_alt?hei=466&wid=466&fmt=webp | Lockable filing cabinet with internal shelving for organised office document and storage management.
18.18.2 | Manifestation/Branding to glass partition | 1 | Item | 150 | 750 | Y | Y | Y | 4LM
18.19 | MEETING ROOM 1 |  | Item
18.19.1 | Chair | 6 | Item | 110 | 660 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%217044592_alt?size=2000,2000&wid=2000&hei=2000&fmt=webp | Mesh visitor chair with fiüed armrests and sled base, suitable for meeting rooms and guest seating.
18.19.2 | TV | 1 | Item | 250 | 250 | Y | Y | Y | www.argos.co.uk/product/7651012?clickPR=plp:15:281 | Meeting room display for presentations and conferencing.
18.19.3 | Manifestation/Branding to glass partition | 1 | Item | 150 | 750 | Y | Y | Y | 5LM
18.20 | MANAGER OFFICE 2 |  | Item
18.20.1 | Filing Cabinet | 1 | Item | 550 | 550 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%213810180_alt?hei=466&wid=466&fmt=webp | Lockable filing cabinet with internal shelving for organised office document and storage management.
18.20.2 | Manifestation/Branding to glass partition | 1 | Item | 150 | 450 | Y | Y | Y | Measures to be confirmed
18.21 | OPEN OFFICE 1 |  | Item
18.21.1 | Pedestal/Drawer | 9 | Item | 480 | 480 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%212067413_alt?size=2000,2000&wid=2000&hei=2000&fmt=webp | Mobile drawer unit for under-desk office storage.
18.21.2 | Filing Cabinet | 3 | Item | 750 | 750 | Y | Y | Y | https://static.viking-direct.co.uk/is/image/odeu13/%217945837_alt?hei=466&wid=466&fmt=webp | Metal filing cabinet with miüed open and enclosed storage compartments for office document organisation.
18.22 | ADDITIONAL ITEMS |  | Item
18.22.1 | TBC |  | Item
| To Summary |  |  |  | 47222.96
Total FF&E

## 7. Summary
Contact Sum Analysis
Project: | Fit-out works
Property: | 191B Park Drive, Milton Park Oxfordshire, OX14
7 | Summary
|  | Quantity | Unit | Rate | Total
1 | GENERAL REQUIREMENTS
2 | PRELIMINARIES | 1 | Item | 73183 | 73183
3 | DESIGN FEES | 1 | Item | 49322.5 | 49322.5
4 | SOW - FABRIC | 1 | Item | 346408.68 | 346408.68
5 | SOW - MEP | 1 | Item | 409107 | 409107
6 | SOW - FF&E | 1 | Item | 47222.96 | 47222.96
Design Devevelopment Risk [5%]
| Main Contractor's Overheads and Profit [Please confirm %] |  |  | 10
Other items if applicable (please list)
| Total Tender Sum (excl. VAT) |  |  |  | 925244.14